SECTION 23 24 33

AIR CURTAINS

This Specification includes Mars Air Systems, LLC; for Mars Cold Storage Series LPV2 air curtains for Walk-In Cooler application. Cold Storage Series air curtains are available for openings 36 inches wide.

Mars Air Curtain products meet the requirements of all North American and European Union Codes and Standards. For a complete selection guide and assistance with your air curtain configuration please visit www.marsair.com.

Important Note: This Specification contains hidden text appearing in red. To show or remove hidden text in MSWord, click the “File” tab or “Office” icon on the top-left corner, select “Options,” select “Display,” and check or uncheck the box marked “Hidden Text.

- GENERAL

  - SECTION INCLUDES

SPECIFIER NOTE - Delete items below not required for project.

    - Air curtains for Walk-In Cooler applications.

  - RELATED SECTIONS

SPECIFIER NOTE - Delete any sections below not relevant to this project; add others as required.

    - Section 05 50 00 - Metal Fabrications: Concealed steel support members.

    - Section 06 10 00 - Rough Carpentry.

    - Section 05 41 00 - Structural Metal Studs.

    - Section 07 62 00 - Sheet metal flashing.

    - Section 07 92 00 - Joint Sealants.

    - Section 08 10 00 – Metal Doors and Frames.

    - Section 08 33 00 - Overhead Coiling Doors.

    - Section 08 42 00 - Entrance Doors.

    - Section 22 10 00 - Plumbing Piping:

    - Section 26 05 00 - Equipment Wiring:  Connections to building power distribution.

  - REFERENCES

SPECIFIER NOTE - Delete items below not required for project.

    - ASTM A240 / A240M -10 – Standard Specification for Chromium and Chromium and Chromium-Nickel Stainless Steel Plate, Sheet, and Strip for Pressure Vessels and for General Applications.

    - ASTM A591 / A591M -98 – Standard Specification for Steel Sheet, Electrolytic Zinc-Coated, for Light Coating Weight (Mass) Application (Withdrawn in 2005, replaced by A879/A879M).

    - ASTM A879 / A879M -06 – Standard Specification for Steel Sheet, Zinc Coated by the Electrolytic Process for Application Requiring Designation of the Coating Mass on Each Surface.

    - ASTM A653 / A653M -09a – Standard Specification for Steel Sheet, Zinc Coated (Galvanized) or Zinc-Iron Alloy-Coated (Galvannealed) by the Hot-Dip Process.

    - CRN – Canadian Registration Number Coil.

    - UL 507 – UL Standard for Safety Electric Fans – Intertek Testing Services Listed for US and Canada

    - NEC – National Electric Code.

  - SUBMITTALS

    - Submit under provisions of Section 01 33 00.

    - Product Data:  Manufacturer's data sheets on each product to be used, including:

      - Preparation instructions and recommendations.

      - Storage and handling requirements and recommendations.

      - Installation methods.

    - Shop Drawings: Include plans, elevations, sections, and details, indicating dimensions, tolerances, materials, fasteners, hardware, finish, piping, electrical wiring diagrams, options, and accessories.

SPECIFIER NOTE - Delete selection samples if colors have already been selected

    - Selection Samples:  For each finish product specified, two complete sets of color chips representing manufacturer's full range of available colors and patterns.

    - Verification Samples:  For each finish product specified, two samples, minimum size 6.25 inches (160 mm) square, representing actual product, color, and patterns.

    - Manufacturer's Certificates: Certify products meet or exceed specified requirements.

    - Operation and Maintenance Manual:  Submit manufacturer's operation and maintenance manual, including operation, maintenance, adjustment, and cleaning instructions, troubleshooting guide, parts list, and electrical wiring diagrams.

  - QUALITY ASSURANCE

    - Manufacturer Qualifications: Minimum ten years documented experience producing the products specified in this Section

    - Installer Qualifications: Minimum five years documented experience installing products specified in this Section

  - DELIVERY, STORAGE, AND HANDLING

SPECIFIER NOTE - Delete items below not required for project

    - Store products in manufacturer's unopened packaging until ready for installation.

    - Store in a dry, heated storage area until installation of products.

    - Protect materials and finish from damage during handling and installation.

  - SEQUENCING

SPECIFIER NOTE - Delete items below not required for project

    - Ensure that locating templates and other information required for installation of products of this section are furnished to affected trades in time to prevent interruption of construction progress.

    - Coordinate the installation of wiring and control switches for air curtains with the openings and the hardware provided for such openings.

    - Install after doors, walls, ceilings and other adjacent surfaces are finished and painted.

  - WARRANTY

SPECIFIER NOTE - Select the applicable warranty from the following paragraphs as required for the unit(s) specified and delete the one not required.

    - LPV2: Standard five-year limited parts warranty for unheated units against defects in workmanship and material.

    - LPV2 with UVP: Standard one year limited parts warranty against defects in workmanship and material.

- PRODUCTS

  - MANUFACTURER

    - Acceptable Manufacturer:  Mars Air Systems, LLC; 14716 South Broadway St., Gardena, CA 90248. Tel: (310) 532-1555 or (800) 421-1266.  Fax: (310) 324-3030.  Email: info@marsair.com.  Web: www.marsair.com._

    - Delete one of the following two paragraphs; coordinate with requirements of Division 1 section on product options and substitutions.

    - Requests for substitutions will be considered in accordance with provisions of Section   01 33 00.

SPECIFIER NOTE - Select the type and sizes required and delete those not required. Indicate the door/opening height for each air curtain on the Drawings or on the Schedule at the end of this Section. If more than one type and/or size is required, indicate the location of each on the Drawings or on the Schedule at the end of this Section-

  - AIR CURTAIN ASSEMBLIES

    - Motor Fan Assembly: Design for easy removal, assembly, repair and maintenance.

      - LPV2 Unit: Motor: Totally enclosed air over (TEAO) cooled motor with sealed lifetime pre-lubricated ball bearings, motor starter and thermal overload protection.

SPECIFIER NOTE - Select one of the following paragraphs and delete the one not required.

        - LPV2 Unit: Wired for variable speed operation.

SPECIFIER NOTE - Select one of the following paragraphs and delete the one not required. Note that Electrical Characteristics below do not include electric heater requirements. Note that all motors listed are based on 60 Hz service. For units wider than 84 inches, refer to submittal for total amps. For other voltages, contact manufacturer.

        - LPV2 Unit: Electrical Characteristics: 115V AC, single phase; 2.4 Amp full load per motor/fan

        - Meets NEC. ETL Listed to conform to UL 507 (US) and CSA22.2 (Canada) Standards.

      - Fans:  Forward curved centrifugal type, double width design, directly driven to an electric motor.

        - Provide resilient isolation dampening mountings between motor frame and housing.

        - Factory balanced blower wheel assembly statically and dynamically.

    - Housing: Self-contained one-piece type with sufficient strength for mounting from pre-punched mounting holes at both ends to ceiling without intermediate support.

      - Size:

SPECIFIER NOTE - Select one of the following paragraphs and delete the ones not required. Heated units are mounted inside only; coordinate with heating paragraphs if required.

        - LPV2 Unit: Unheated: 8-7/8 inches deep by 8 inches high (including discharge nozzle) by width of unit

      - Mounting:

SPECIFIER NOTE - Select one of the following paragraphs and delete the ones not required. Heated units are mounted inside only; coordinate with heating paragraphs if required.

        - Unheated Inside Mount

        - Mount Location Indicated.

      - Material:

SPECIFIER NOTE - Select one of the following two paragraphs and delete the one not required.

        - Provide 18- and 20-gauge electro or hot dipped galvanized steel sheet housing conforming to ASTM A 591 and/or ASTM A 653.

      - Air Inlet Grille and Filters:

        - LPV2

          - Location: Front.

          - Type: Fixed air intake grille.

        - LPV2 with UVP

          - Location: Front.

          - Type: UV Only as follows

            - UV: UVC & UVV germicidal and odor elimination

SPECIFIER NOTE - Select one of the following air inlet type paragraphs and delete the ones not required.

      - Discharge: Provide integral discharge nozzle specified.

SPECIFIER NOTE - Select following paragraph for sheet steel housings only. Delete entirely for stainless steel housing. Select color required for steel housing and delete the ones not required.

      - Finish and Color: Provide with, no VOC, corrosion resistant polyurethane powder coated finish for sheet metal housings.

        - LPV2 Unit:

          - Obsidian Black.

          - Pearl White.

    - Environmental Air Curtains: Models for Heights up to 8 feet (2438 mm) for Environmental Separation and Temperature Control and up to 7 feet (2133 mm) for Flying Insect Control.:

      - Discharge Nozzle:  Adjustable air foil vanes with a plus/minus 40 degree sweep front to back.

      - Air Velocity at Nozzle:

SPECIFIER NOTE - Select one of the following paragraphs for the model required and delete the ones not required. If more than one type is required show the location of each type on the Drawings or on the Schedule at the end of this Section

        - LPV236-1: 36 Inch (915 mm) Wide Units: 1800 feet/min (9.1 m/s) single 1/6HP motor/fan assembly.

      - Air Speed at Floor: Minimum of 400 fpm (2 m/s) at 1 foot (304 mm) from the floor.

      - Air Inlet Grille and Filters:

        - Location: Front.

SPECIFIER NOTE - Select one of the following air inlet type paragraphs and delete the ones not required.

        - Type: Fixed air intake grille.

SPECIFIER NOTE - Include the following optional filter paragraph if required and delete if not required.

        - Speed: 625 cu ft/min (295 L/s), minimum, per motor/fan assembly.

      - Sound Pressure Level At 10 feet (3 m) From Nozzle:

SPECIFIER NOTE - Select one of the following paragraphs and delete the ones not required. Coordinate selection with the Model specified above.

        - LPV236: Single Motor/Fan Units:  49 dBA.

  - COMPONENTS

    - LPV2: Solid State Controller for Unheated Units: Recommended for units whenever a door limit switch or automatic ON/OFF controls is used to automatically start and stop the air curtain. Provide controller as follows:

      - Mounting: Factory mounted and wired inside air curtain housing.

      - Electrical components UL/CUL listed.

      - Single point connection

      - LPV2 Unit: Adjustable time delay built in for Fan delayed OFF on door closure

    - LPV2 with UVP: Provide complete with motor control panel factory mounted to air curtain housing.

      - Mounting: Factory mounted and wired inside air curtain housing.

      - Electrical components UL/CUL listed.

      - Single point connection

  - CONTROLS

    - Door-Activated Limit switch(s): Automatic on/off control, activates air curtain when door is opened and turns off when door is closed.

      - Type: Magnetic reed switch and actuator included.

      - Operation for Unheated Units: Automatic on/off control, on when door is opened, off when door is closed.

    - Door-Activated Limit switch(s):  Automatic on/off control, activates air curtain when door is opened and turns off when door is closed.

      - Type: Magnetic reed switch and actuator for swing and sliding doors.

        - 24V (low voltage) controls for door activation

        - Factory mounted and wired controls for door activation

      - Operation for UVP Units:  Automatic control, UV ON with Fan at High Speed when door is opened, UV ON with Fan at Low Speed when door is closed.

        - Field adjustable Low speed

        - ON/OFF switch for UV

        - ON/OFF switch to turn unit OFF

        - Safety kill switch to turn unit OFF during service

- EXECUTION

  - EXAMINATION

    - Verify that required utilities are in correct location and are of correct capacities for specified products.

    - Verify openings to receive air curtains are plumb, level, square, accurately aligned, correctly located, and in tolerance.

    - Examine surfaces to receive air curtains. If surface preparation is the responsibility of another installer, notify Architect of unsatisfactory preparation before proceeding.

  - INSTALLATION

SPECIFIER NOTE - Indicate the mounting location(s) on the Drawing or on the Schedule at the end of this Section. Units are typically wall mounted horizontally above the door opening.  Units can also be suspension mounted from the ceiling or vertically mounted alongside the opening.  Heated units must be mounted on the inside or protected side of the opening.

    - Install air curtains in accordance with approved shop drawings and manufacturer's printed installation instructions.

    - Install air curtains plumb, level, square, true to line, and weathertight, without warp or rack.

    - Anchor air curtains securely in place to supports.

    - Coordinate with sheet metal flashing as specified in Section 07 62 00.

    - Install joint sealants as specified in Section 07 92 00.

    - Coordinate with electrical power as specified in Section 26 05 00.

    - Install door limit switches and adjust for correct operation.

    - Provide connection to piped services and utilities as specified in Section 22 10 00 and 23 21 00.

  - FIELD QUALITY CONTROL

    - Adjust air curtains to function properly.

    - Adjust air foil vanes located within the discharge nozzle as required for prevailing conditions at each opening.

  - CLEANING

    - Clean air curtains promptly after installation in accordance with manufacturer's instructions.

    - Repair minor damages to finish in accordance with manufacturer's instructions and as approved by Architect.

    - Remove and replace damaged components that cannot be successfully repaired as determined by Architect.

  - PROTECTION

    - Protect materials and finish from damage until substantial completion.

SPECIFIER NOTE - For facilities with multiple types and sizes of air curtains use an Air Curtain Schedule to list requirements for each size, type, HP, and power requirements of air curtain(s) required. Delete if not required.

  - SCHEDULES

    - Refer to Air Curtain Schedule appended to this section.

END OF SECTION