SECTION 23 34 33

AIR CURTAINS

This specification includes Mars Air Systems High Velocity Series 2 air curtains for environmental control, flying insect control, and temperature control. Heating options are available for the HV2 series for electric, hot water, steam, and indirect fired gas.

High Velocity Series 2 air curtains are available for openings 36 inches to 144 inches wide and come in two varieties: the HV2 series for environmental and flying insect control, and the NH2 series for flying insect control (ETL Sanitation). Recommended installation heights for the HV2 series are up to 14 feet for environmental separation and temperature control applications and up to 12 feet for flying insect control applications. Maximum installation height for the NH2 series is 7 feet for flying insect control (ETL Sanitation). High Velocity Series 2 air curtains are typically effective to resist wind loads up to 12 mph for temperature control applications. Note that velocities specified for each unit are based on a 60 Hz power source.

Typical installations include mid-size dock doors and receiving doors. Air curtains help reduce heating and cooling costs while expediting the flow of traffic from one work area to another or in and out of a building. At the same time, air curtains can repel mild breeze and minimize the entrance of windborne dust, fumes, pollutants, and flying insects.

Mars Air Curtain products meet the requirements of all North American and European Union Codes and Standards. For a complete selection guide and assistance with your air curtain configuration, please visit www.marsair.com.

Important Note: This specification contains hidden text appearing in red. To show or remove hidden text in MSWord, click the “File” tab or “Office” icon on the top-left corner, select “Options,” select “Display,” and check or uncheck the box marked “Hidden Text.”

- GENERAL

  - SECTION INCLUDES

SPECIFIER NOTE – Delete items below not required for project.

    - Air curtains for pedestrian entrances.

    - Air curtains for vehicular entrances.

    - Air curtains for large loading dock doors.

  - RELATED SECTIONS

SPECIFIER NOTE – Delete any sections below not relevant to this project; add others as required.

    - Section 05 50 00 – Metal Fabrications: Concealed steel support members.

    - Section 06 10 00 – Rough Carpentry.

    - Section 05 41 00 – Structural Metal Studs.

    - Section 07 62 00 – Sheet metal flashing.

    - Section 07 92 00 – Joint Sealants.

    - Section 08 10 00 – Metal Doors and Frames.

    - Section 08 33 00 – Overhead Coiling Doors.

    - Section 08 42 00 – Entrance Doors.

    - Section 22 10 00 – Plumbing Piping:

    - Section 23 21 00 – Hydronic Piping: Hot water heating piping to units.

    - Section 23 22 13- Steam and Condensate Piping: Steam heating piping to units.

    - Section 26 05 00 – Equipment Wiring: Connections to building power distribution.

  - REFERENCES

SPECIFIER NOTE – Delete items below not required for project.

    - ASTM A240 / A240M -10 – Standard Specification for Chromium and Chromium.

    - ASTM A591 / A591M -98 – Standard Specification for Steel Sheet, Electrolytic Zinc-Coated, for Light Coating Weight (Mass) Application (Withdrawn in 2005, replaced by A879/A879M).

    - ASTM A879 / A879M -06 – Standard Specification for Steel Sheet, Zinc Coated by the Electrolytic Process for Application Requiring Designation of the Coating Mass on Each Surface.

    - ASTM A653 / A653M -09a – Standard Specification for Steel Sheet, Zinc Coated (Galvanized) or Zinc-Iron Alloy-Coated (Galvannealed) by the Hot-Dip Process.

    - AHRI 410-2001 – Standard for Forced-Circulation Air-cooling and Air-Heating Coils.

    - NSF/ANSI 37 – Air Curtains for entranceways in food and food service establishments – ETL Sanitation.

    - CRN – Canadian Registration Number Coil.

    - ANSI Z223-NFPA 54 – National Fuel Gas Code/

    - NEC – National Electric Code.

  - SUBMITTALS

    - Submit under provisions of Section 01 33 00.

    - Product Data: Manufacturer's data sheets on each product to be used, including:

      - Preparation instructions and recommendations.

      - Storage and handling requirements and recommendations.

      - Installation methods.

    - Shop Drawings: Include plans, elevations, sections, and details, indicating dimensions, tolerances, materials, fasteners, hardware, finish, piping, electrical wiring diagrams, options, and accessories.

SPECIFIER NOTE – Delete the following paragraphs if LEED is not applicable. Review design-phase credits available related to tubular unit skylights, including contribution to IEQ Cr 6.1 Controllability of Systems, IEQ Cr 8.1. Daylighting, EA Cr 1 Energy Optimization, and ID Cr 1 Innovation in Design credits. Consult VELUX representative for detailed support data.

    - LEED Submittals: Provide documentation of how the requirements of Credit will be met:

      - List of proposed materials with recycled content. Indicate post-consumer recycled content and pre-consumer recycled content for each product having recycled content.

      - Product data and certification letter indicating percentages by weight of post-consumer and pre-consumer recycled content for products having recycled content.

SPECIFIER NOTE – Delete selection samples if colors have already been selected.

    - Selection Samples: For each finish product specified, two complete sets of color chips representing manufacturer's full range of available colors and patterns.

    - Verification Samples: For each finish product specified, two samples, minimum size 6.25 inches (160 mm) square, representing actual product, color, and patterns.

    - Manufacturer's Certificates: Certify products meet or exceed specified requirements.

    - Operation and Maintenance Manual: Submit manufacturer's operation and maintenance manual, including operation, maintenance, adjustment, and cleaning instructions, troubleshooting guide, parts list, and electrical wiring diagrams.

  - QUALITY ASSURANCE

    - Manufacturer Qualifications: Minimum ten years documented experience producing the products specified in this Section

    - Installer Qualifications: Minimum five years documented experience installing products specified in this Section

  - DELIVERY, STORAGE, AND HANDLING

SPECIFIER NOTE – Delete items below not required for project.

    - Store products in manufacturer's unopened packaging until ready for installation.

    - Store in a dry, heated storage area until installation of products.

    - Protect materials and finish from damage during handling and installation.

  - SEQUENCING

SPECIFIER NOTE – Delete items below not required for project.

    - Ensure that locating templates and other information required for installation of products of this section are furnished to affected trades in time to prevent interruption of construction progress.

    - Coordinate the installation of wiring and control switches for air curtains with the openings and the hardware provided for such openings.

    - Install after doors, walls, ceilings, and other adjacent surfaces are finished and painted.

  - WARRANTY

SPECIFIER NOTE – Select the applicable warranty from the following paragraphs as required for the unit(s) specified and delete the one not required.

    - Standard five-year limited parts warranty for unheated units against defects in workmanship and material.

    - Standard 18-month limited parts warranty for heated units against defects in workmanship and materials.

- PRODUCTS

  - MANUFACTURER

    - Acceptable Manufacturer: Mars Air Systems, LLC; 14716 South Broadway St., Gardena, CA 90248. Tel: (310) 532-1555 or (800) 421-1266. Fax: (310) 324-3030. Email: info@marsair.com. Web: www.marsair.com.

    - Delete one of the following two paragraphs: coordinate with requirements of Division 1 section on product options and substitutions.

    - Requests for substitutions will be considered in accordance with provisions of Section 01 33 00.

SPECIFIER NOTE – Select the type and sizes required and delete those not required. Indicate the door/opening height for each air curtain on the Drawings or on the Schedule at the end of this Section. If more than one type and/or size is required, indicate the location of each on the Drawings or on the Schedule at the end of this Section.

  - AIR CURTAIN ASSEMBLIES

    - Motor Fan Assembly: Design for easy removal, assembly, repair, and maintenance.

      - Motor: Totally enclosed air over (TEAO) cooled motor with sealed lifetime pre-lubricated ball bearings, motor starter and thermal overload protection.

        - Wired for single speed operation.

        - Wired for two speed operation.

SPECIFIER NOTE – Select one of the following paragraph(s) as required for specialty motors and delete the one not required. Indicate the location of special use motors on the Drawings or on the Schedule at the end of this Section.

        - Provide wash down type motors, NEC IP-54 for the locations indicated.

        - Provide explosion proof type motors, NEC Class 1, Division 1, Group D for the locations indicated.

SPECIFIER NOTE – Select one of the following four paragraphs and delete the ones not required. Note that Electrical Characteristics below do not include electric heater requirements. Note that all motors listed are based on 60 Hz service. For other voltages contact manufacturer.

        - Electrical Characteristics: 115V AC, single phase; 9.0 Amp full load per motor/fan.

        - Electrical Characteristics: 208/230V AC, single phase; 5.0 Amp full load per motor/fan.

        - Electrical Characteristics: 208/230V AC, three-phase; 3.3/3.2 Amp full load per motor/fan.

        - Electrical Characteristics: 460V AC, three-phase; 1.6 Amp full load per motor/fan.

        - Electrical Characteristics: 575V AC, three-phase; 1.3 Amp full load per motor/fan.

        - Meets NEC. ETL Listed to conform to UL 507 (US) and CSA22.2 (Canada) Standards. AMCA 211 Certified.

      - Fans: Forward curved centrifugal type, double width, and double inlet design, directly driven to an electric motor.

        - Provide resilient isolation dampening mountings between motor frame and motor mounting pan

        - Factory balanced blower wheel assembly statically and dynamically.

    - Housing: Self-contained one-piece type with sufficient strength for mounting from pre-punched mounting holes at both ends to adjacent walls or ceiling without intermediate support.

      - Size:

SPECIFIER NOTE – Select one of the following paragraphs and delete the ones not required. Heated units are mounted inside only; coordinate with heating paragraphs if required.

        - Unheated: 15-5/8 inches deep by 14 inches high (including discharge nozzle) by width of unit.

        - Electric Heated: 21-3/8 inches deep by 14 inches high (including discharge nozzle) by width of unit.

        - Hot Water/Steam Heated: 21-3/8 inches deep by 14 inches high (including discharge nozzle) by width of unit plus 10 inches for manifolds.

        - Indirect Fired Gas Heated: 68 1/8 inches deep by 34 inches high (including discharge nozzle) by width of unit.

      - Mounting:

SPECIFIER NOTE – Select one of the following paragraphs and delete the ones not required. Heated units are mounted inside only; coordinate with heating paragraphs if required.

        - Unheated Inside Mount.

        - Heated Inside Mount.

        - Unheated Outside Mount.

        - Mount Location Indicated.

      - Material:

SPECIFIER NOTE – Select one of the following paragraphs and delete the one not required.

        - Provide 18- and 20-gauge electro or hot dipped galvanized steel sheet housing conforming to ASTM A 591 and/or ASTM A 653.

        - Provide type 304 stainless steel housing with brushed finish. ASTM A 240/A 240M.

      - Air Inlet Grille and/or Filters: Provide air inlet grille and/or filters specified.

      - Discharge: Provide integral discharge nozzle specified.

SPECIFIER NOTE – Select following paragraph for sheet steel housings only. Delete entirely for stainless steel housing. Select color required for steel housing and delete the ones not required. Titanium Silver is standard.

      - Finish and Color: Provide with, no VOC, corrosion resistant polyurethane powder coated finish for sheet metal housings.

        - Titanium Silver

        - Obsidian Black.

        - Pearl White.

        - Stainless Steel.

    - Environmental Air Curtains: Models for Heights up to 14 feet (4267 mm) for Environmental Separation and Temperature Control and up to 12 feet (3656 mm) for Flying Insect Control.

      - Discharge Nozzle: Adjustable air foil vanes with a plus/minus 40-degree sweep front to back.

      - Air Velocity at Nozzle:

SPECIFIER NOTE – Select one of the following paragraphs for the model required and delete the ones not required. If more than one type is required show the location of each type on the Drawings or on the Schedule at the end of this Section.

        - HV236-1: 36 Inch (915 mm) Wide Units: 2745 feet/min (13.9 m/s) single 1HP motor/fan assembly.

        - HV242-1: 42 Inch (1065 mm) Wide Units: 2654 feet/min (13.5 m/s) single 1HP motor/fan assembly.

        - HV248-1: 48 Inch (1220 mm) Wide Units: 2447 feet/min (12.4 m/s) single 1HP motor/fan assembly.

        - HV260-1: 60 Inch (1524 mm) Wide Units: 2208 feet/min (11.2 m/s) single 1HP motor/fan assembly.

        - HV272-2: 72 Inch (1830 mm) Wide Units: 2745 feet/min (13.9 m/s) two 1HP motor/fan assemblies.

        - HV284-2: 84 Inch (2133 mm) Wide Units: 2654 feet/min (13.5 m/s) two 1HP motor/fan assemblies.

        - HV296-2: 96 Inch (2440 mm) Wide Units: 2447 feet/min (12.4 m/s) two 1HP motor/fan assemblies.

        - HV2108-3: 108 Inch (2743 mm) Wide Units: 2745 feet/min (13.9 m/s) two 1HP motor/fan assemblies.

        - HV2120-2: 120 Inch (3050 mm) Wide Units: 2208 feet/min (11.2 m/s) two 1HP motor/fan assemblies.

        - HV2120-3: 120 Inch (3050 mm) Wide Units: 2678 feet/min (13.6 m/s) three 1HP motor/fan assemblies.

        - HV2144-3: 144 Inch (3660 mm) Wide Units: 2447 feet/min (12.4 m/s) three 1HP motor/fan assemblies.

      - Air Inlet Grille and Filters:

        - Location: Front.

SPECIFIER NOTE – Select one of the following air inlet type paragraphs and delete the ones not required.

        - Type: Fixed air intake grille.

SPECIFIER NOTE – Include the following optional filter paragraph if required and delete if not required.

          - Filter: Aluminum mesh, 1/4 inch (6.4 mm), washable.

        - Type: Filter Only as follows:

SPECIFIER NOTE – Include one of the following optional filter paragraphs as required and delete those not required.

          - Filter: Flat bank 1-inch, disposable.

          - Filter: Flat bank 2-inch, disposable.

          - Filter: Aluminum mesh, 1/4 inch (6.4 mm), washable.

        - Speed: 4000 cu ft/min (1888 L/s), minimum, per motor/fan assembly.

      - Sound Pressure Level At 10 feet (3 m) From Nozzle:

SPECIFIER NOTE – Select one of the following paragraphs and delete the ones not required. Coordinate selection with the Model specified above.

        - Single Motor/Fan Units: 70 dBA.

        - Two Motor/Fan Units: 73 dBA.

        - Three Motor/Fan Units: 75 dBA.

        - Four Motor/Fan Units: 75 dBA.

    - Insect Control Air Curtains: Models for Service Entry Heights to 7 feet (2134 mm) certified to NSF/ANSI Standard 37.

      - Discharge Nozzle: Wedge-shaped discharge outlet nozzle with adjustable air foil vanes with a plus/minus 40-degree sweep front to back.

      - Air Velocity at Nozzle:

SPECIFIER NOTE – Select one of the following paragraphs for the model required and delete the ones not required. If more than one type is required show the location of each type on the Drawings or on the Schedule at the end of this Section.

        - NH236-1: 36 Inch (915 mm) Wide Units: 2745 feet/min (13.9 m/s) single 1HP motor/fan assembly.

        - NH242-1: 42 Inch (1065 mm) Wide Units: 2654 feet/min (13.5 m/s) single 1HP motor/fan assembly.

        - NH248-1: 48 Inch (1220 mm) Wide Units: 2447 feet/min (12.4 m/s) single 1HP motor/fan assembly.

        - NH260-1: 60 Inch (1524 mm) Wide Units: 2208 feet/min (11.2 m/s) single 1HP motor/fan assembly.

        - NH272-2: 72 Inch (1830 mm) Wide Units: 2745 feet/min (13.9 m/s) single 1HP motor/fan assembly.

        - NH284-2: 84 Inch (2133 mm) Wide Units: 2654 feet/min (13.5 m/s) single 1HP motor/fan assembly.

        - NH296-2: 96 Inch (2440 mm) Wide Units: 2447 feet/min (12.4 m/s) single 1HP motor/fan assembly.

        - NH2108-3: 108 Inch (2743 mm) Wide Units: 2745 feet/min (13.9 m/s) single 1HP motor/fan assembly.

        - NH2120-2: 120 Inch (3050 mm) Wide Units: 2208 feet/min (11.2 m/s) single 1HP motor/fan assembly.

        - NH2120-3: 120 Inch (3050 mm) Wide Units: 2678 feet/min (13.6 m/s) single 1HP motor/fan assembly.

        - NH2144-3: 14 Inch (3660 mm) Wide Units: 2447 feet/min (12.4 m/s) single 1HP motor/fan assembly,

      - Air Speed at Floor:

        - Service entry doors require a minimum of 1600 fpm (8.13 m/s) at 3 feet (914 mm) from floor.

      - Air Inlet Grille and Filters:

        - Location: Front.

        - Speed: 4000 cu ft/min (1888 L/s), minimum, per motor/fan assembly.

        - Type: Fixed air intake grille.

      - Sound Pressure Level At 10 feet (3 m) From Nozzle:

        - Single Motor/Fan Units: 70 dBA.

SPECIFIER NOTE – Select the optional components required from the following paragraphs for the air curtains specified. If more than one type of air curtain or component is required, indicate the location of each curtain and the components required for each location on the Drawings or on the Schedule at the end of this Section. Contact Mars Air Systems for specialty steam and hot water heaters other than those included in the specification.

  - COMPONENTS

    - Electric Heaters: Provide complete with motor control panel factory mounted to air curtain housing, and thermostat to be field installed.

      - Temperature limit controller.

      - Thermostat: Wall-mounted, 24-Volt operation, with heater on/off selection.

      - Heating Coils: Electrical components UL/CUL listed.

    - Steam Heaters: Provide finned tube steam coils for field mounting on air intake side of the air curtain cabinet with opposite end connections.

SPECIFIER NOTE – Select one of the following paragraphs.

      - Output: Air curtain manufacturer's standard, one-row coils.

      - Output: Air curtain manufacturer's standard, two-row coils.

      - Coils: Certified in accordance with AHRI 410.

SPECIFIER NOTE – Selcet one of the following connections paragraphs.

      - Connections: Opposite end.

      - Connections: Same end, right hand.

      - Connections: Same end, left hand.

      - Casing: One-piece unpainted galvanized steel, bolted to air curtain housing.

      - Supply and return fittings on ends of casing.

      - Steam Distributing coil required for 8 feet and above for same end coils. Dual supply, Single returns.

SPECIFIER NOTE – Thermostat is optional. Delete if not required.

      - Thermostat: Wall-mounted, 110-Volt operation, with heater on/off selection.

      - Thermostat: Wall-mounted, 208/230-Volt operation, with heater on/off selection.

    - Hot Water Heaters: Provide finned tube water coils for field mounting on air intake side of the air curtain cabinet with opposite end connections.

SPECIFIER NOTE – Select one of the following output paragraphs.

      - Output: Air curtain manufacturer's standard, one-row coils.

      - Output: Air curtain manufacturer's standard, two-row coils.

      - Coils: Certified in accordance with AHRI 410.

SPECIFIER NOTE – Select one of the following connections paragraphs.

      - Connections: Opposite end.

      - Connections: Same end, right hand.

      - Connections: Same end, left hand.

      - Casing: One-piece unpainted galvanized steel, bolted to air curtain housing.

      - Supply and return fittings on ends of casing.

SPECIFIER NOTE – Thermostat is optional. Delete if not required.

      - Thermostat: Wall-mounted, 110-Volt operation, with heater on/off selection.

      - Thermostat: Wall-mounted, 208/230-Volt operation, with heater on/off selection.

    - Gas Heaters: Provide field mounted indirect natural gas fired, power vented duct furnace, with aluminized steel heat exchanger and die-formed stainless steel insert burners; manifolds, orifices, flame sensor, and igniter easily removable as an assembly.

      - Output: Air curtain manufacturer's standard.

      - Complies with:

        - Canadian Standards Association (CSA) labeled for US and Canadian application.

        - ANSI Z223/NFPA 54 National Fuel Gas Code.

        - CAN/CGA B149.1 Installation Codes for Natural Gas Burning Appliances and Equipment.

      - Fuel Type: Provide orifices for:

SPECIFIER NOTE – Select fuel type required and delete the one not required.

        - Natural gas.

        - LP.

      - 24 V control voltage transformer.

      - Combination single-stage gas control system with regulated combination redundant gas valve and intermittent spark pilot with electronic flame supervision.

      - Optional 2 stage.

      - Optional Modulation Gas.

      - Limit and safety controls.

SPECIFIER NOTE Thermostat is optional. Delete if not required.

      - Thermostat: Wall-mounted, 24-Volt operation, with heater on/off selection.

SPECIFIER NOTE – Select one of the following Motor Control Panel paragraphs as required and delete the ones not required. The first paragraph is for Unheated Units, the second is for Electric Heated Units, the third is for Steam or Hot Water Heated Units and the fourth is for Gas Heated Units.

    - Motor Control Panels for Unheated Units: Recommended for all three-phase units and single-phase units with combined motor capacities of more than 1 HP whenever a door limit switch is used to automatically start and stop the air curtain. Provide motor control panels as follows:

SPECIFIER NOTE – Delete all but one of the following three mounting paragraphs. Standard mounting offering for motor control panel is shipped loose for field mounting.

      - Mounting: Shipped loose to be field mounted.

      - Mounting: Factory mounted on right hand side of air curtain housing.

      - Mounting: Factory mounted on left hand side of air curtain housing.

      - Electrical components UL/CUL listed.

      - Optional Digital Programmable Controller:

        - WiFi enabled controller for wireless interface with field supplied smartphone, tablet or computer

        - No download or app required for wireless interface

        - Wireless control range up to minimum of 50 feet from controller

        - Fully factory assembled and wired inside the air curtain for easy field installation

        - Optional remote mounted high resolution 7” Color LCD Display with resistive touchscreen technology

        - Fully programmable controller

        - Pre-set and fully customizable programs

        - Time delay (Passive & Adaptive)

        - 24/7/365 timer

        - Maintenance schedule alerts

        - Password protected

        - Low voltage control signal for door activation

        - Multispeed fan control

        - Optional VFD compatible with 0-10VDC output

        - Optional Integrated BMS controls

        - Optional BACnet MS/TP

        - Optional BACnet IP

        - Optional adaptive fan speed control based on existing field conditions. Field mounted outdoor temperature sensors required.

    - Motor Control Panels for Electric Heated Units: Motor Control Panel is included for all electric heated units. Thermostat is provided for field installation. Provide motor control panels as follows:

SPECIFIER NOTE – Delete all but one of the following three mounting paragraphs. Standard factory mounting for motor control panel on electric heated units is on the inside of air curtain housing.

      - Mounting: Factory mounted on the inside of air curtain housing.

      - Mounting: Factory mounted on right hand side of air curtain housing

      - Mounting: Factory mounted on left hand side of air curtain housing.

      - Electrical components UL/CUL listed.

      - Optional Digital Programmable Controller:

        - WiFi enabled controller for wireless interface with field supplied smartphone, tablet or computer

        - No download or app required for wireless interface

        - Wireless control range up to minimum of 50 feet from controller

        - Fully factory assembled and wired inside the air curtain for easy field installation

        - Optional remote mounted high resolution 7” Color LCD Display with resistive touchscreen technology

        - Fully programmable controller

        - Pre-set and fully customizable programs

        - Time delay (Passive & Adaptive)

        - Factory Integrated temperature control sensors. No external thermostat required.

        - Heat on Demand Mode to regulate the space temperature

        - Summer-Winter modes

        - 24/7/365 timer

        - Maintenance schedule alerts

        - Password protected

        - High temperature lock from fan failure

        - Low voltage control signal for door activation

        - Multispeed fan control

        - Optional VFD compatible with 0-10VDC output

        - Optional Integrated BMS controls

        - Optional BACnet MS/TP

        - Optional BACnet IP

        - Optional adaptive fan speed control and heat control based on existing field conditions. Field mounted outdoor temperature sensors required.

    - Motor Control Panels for Hot Water and Steam Heated Units: Recommended for all three-phase units and single phase units with combined motor capacities of more than 1HP whenever a door limit switch is used to automatically start and stop the air curtain. Provide motor control panels as follows:

SPECIFIER NOTE – Delete all but one of the following three mounting paragraphs.

      - Mounting: Shipped loose to be field mounted.

      - Mounting: Factory mounted on right hand side of air curtain housing.

      - Mounting: Factory mounted on left hand side of air curtain housing.

      - Provide with remote mount thermostat for field installation.

      - Electrical components UL/CUL listed.

      - Panels UL 508A listed.

      - Optional Digital Programmable Controller:

        - WiFi enabled controller for wireless interface with field supplied smartphone, tablet or computer

        - No download or app required for wireless interface

        - Wireless control range up to minimum of 50 feet from controller

        - Fully factory assembled and wired inside the air curtain for easy field installation

        - Optional remote mounted high resolution 7” Color LCD Display with resistive touchscreen technology

        - Fully programmable controller

        - Connect and control via any web browser

        - Factory built wireless router with over 50 feet range

        - Pre-set and fully customizable programs

        - Time delay (Passive & Adaptive)

        - Factory Integrated temperature control sensors. No external thermostat required.

        - Heat on Demand Mode to regulate the space temperature

        - Summer-Winter modes

        - 24/7/365 timer

        - Maintenance schedule alerts

        - Password protected

        - High temperature lock from fan failure

        - Low voltage control signal for door activation

        - Multispeed fan control

        - Optional VFD compatible with 0-10VDC output

        - Optional Integrated BMS controls

        - Optional BACnet MS/TP

        - Optional BACnet IP

        - Optional adaptive fan speed control and heat control based on existing field conditions. Field mounted outdoor temperature sensors required.

    - Motor Control Panels for Gas Heated Units: Recommended for all units whenever a door limit switch is used to automatically start and stop the air curtain. Optional motor control panel and thermostat for field installation. Provide motor control panel as follows:

SPECIFIER NOTE – Motor Control Panel with integrated thermostat is optional. Delete if not required.

      - Control Panel: Includes increased transformer for power venter(s) with integrated 24-Volt thermostat with furnace and motor controls.

SPECIFIER NOTE – Select the following thermostat paragraph if optional control panel paragraph is selected. Delete if not required.

      - Thermostat: Wall-mounted, 24-Volt operation, with heater on/off selection

SPECIFIER NOTE – Delete all but one of the following mounting paragraphs. Motor control panel for gas heated units are integrated with a heater control. Motor control panel is shipped loose to be field mounted.

      - Mounting: Shipped loose to be field mounted.

      - Mounting: Factory mounted on right hand side of air curtain housing.

      - Mounting: Factory mounted on left hand side of air curtain housing.

      - Provide with remote mount thermostat for field installation.

      - Electrical components UL/CUL listed.

      - Panels UL 508A listed.

    - Door-Activated Limit switch(s): Provide, field installed 250-Volts, 20 amps limit switch to control air curtain(s) as follows; Automatic on/off control, activates air curtain when door is opened and turns off when door is closed. Provide limit switch for direct control one 1 HP or up to two 1/2 HP single phase motors without a separate control panel. Provide a separate control panel for three-phase motors and/or units exceeding 1 HP, 250-Volts or 20 amps controlled by a limit switch.

      - Type: Combination plunger/roller switch for swing and sliding doors.

SPECIFIER NOTE – Delete three of the following four paragraphs to suit enclosures for incidental contact, protection against weather and corrosive exposure and explosion proof as required.

        - Provide limit switches with NEMA 1 (20 amps) ratings in locations indicated.

        - Provide limit switches with NEMA 4X (10 amps) ratings in locations indicated.

        - Provide limit switches with NEMA 4X (15 amps) ratings in locations indicated.

        - Provide limit switches with NEMA 7 (10 amps) ratings in locations indicated.

SPECIFIER NOTE – Edit the following two paragraphs to suit the units specified. Delete the paragraph not applicable if it is not required.

      - Type: Magnetic reed switch and actuator for swing and sliding doors. Industrial floor mounted or surface mounted switches for roll up doors.

      - Operation for Unheated Units: Automatic on/off control, on when door is opened, off when door is closed.

      - Operation for Heated Units: Automatic on when door is opened, off after time delay period after door is closed, maintaining heat in the event door is opened within time delay period. Field adjustable from 1 to 17 minutes.

      - Operation for Gas Heated Units: Automatic on when door is opened, off after time delay period (60 seconds) after door is closed.

    - Provide mounting hardware as required for the opening.

- EXECUTION

  - EXAMINATION

    - Verify that required utilities are in correct location and are of correct capacities for specified products.

    - Verify openings to receive air curtains are plumb, level, square, accurately aligned, correctly located, and in tolerance.

    - Examine surfaces to receive air curtains. If surface preparation is the responsibility of another installer, notify Architect of unsatisfactory preparation before proceeding.

  - INSTALLATION

SPECIFIER NOTE – Indicate the mounting location(s) on the Drawing or on the Schedule at the end of this Section. Units are typically wall mounted horizontally above the door opening. Units can also be suspension mounted from the ceiling or vertically mounted alongside the opening. Heated units must be mounted on the inside or protected side of the opening.

    - Install air curtains in accordance with approved shop drawings and manufacturer's printed installation instructions.

    - Install air curtains plumb, level, square, true to line, and weathertight, without warp or rack.

    - Anchor air curtains securely in place to supports.

    - Coordinate with sheet metal flashing as specified in Section 07 62 00.

    - Install joint sealants as specified in Section 07 92 00.

    - Coordinate with electrical power as specified in Section 26 05 00.

    - Install door limit switches and adjust for correct operation.

    - Provide connection to piped services and utilities as specified in Section 22 10 00 and 23 21 00.

  - FIELD QUALITY CONTROL

    - Adjust air curtains to function properly.

    - Adjust air foil vanes located within the discharge nozzle as required for prevailing conditions at each opening.

    - Check heated air curtain performance on a calm day by measuring air temperature 6 inches off the floor. Optimal reading is halfway between the temperature inside and outside the building.

  - CLEANING

    - Clean air curtains promptly after installation in accordance with manufacturer's instructions.

    - Repair minor damages to finish in accordance with manufacturer's instructions and as approved by Architect.

    - Remove and replace damaged components that cannot be successfully repaired as determined by Architect.

  - PROTECTION

    - Protect materials and finish from damage until substantial completion.

SPECIFIER NOTE – For facilities with multiple types and sizes of air curtains use an Air Curtain Schedule to list requirements for each size, type, HP, and power requirements of air curtain(s) required. Delete if not required.

  - SCHEDULES

    - Refer to Air Curtain Schedule appended to this section.

END OF SECTION